Active Power Controls

MFRS.: AUTOMATIC VOLTAGE CONTROLLER, ISOLATION & AUTO TRANSFORMERS & LT PANEL

Plant Address:- A-178 MIDC Chincholi, Solapur, Maharastra- 413255

Mobile No.:- +91-8888958904,+91-9423777810,+91-9011485679

Email:activepowercontrol9@gmail.com	Website: https://activepowercontrol.lovable.app/

# Operations & Maintenance (O&M) Manual

- Equipment Handling & Storage

  - Offloading: Always utilize the welded lifting lugs located on the top panel of the tank cover. Avoid passing chains around the radiator tubes or thin outer sheet steel walls.

  - Storage Environment: If storing prior to commissioning, ensure the unit is kept in a dry, dust-free zone. Ensure all protective conduit plugs remain tightly sealed.

- Commissioning Procedure

  - Foundation: Install the unit perfectly level on a reinforced concrete plinth designed to bear the structural operating weights detailed in Section 4

  - Earthing: Securely connect the two designated diagonal body earth terminals to separate dedicated site ground grids.

  - Control Loop Calibration: Energize the low-voltage auxiliary control circuits. Verify that the tracking voltmeter boots up accurately and the electronic sensing relays operate correctly.

- Periodic Maintenance Matrix

| Frequency | Target Component | Maintenance Action Required |
| --- | --- | --- |
| Daily | Voltmeter Panels & Gauges | Log input/output operational terminal line matrix and inspect oil level indicators. |
| Monthly | Roller Contacts & Tracks | Inspect carbon roller assemblies for mechanical wear tracks. Blow out any accumulation of carbon dust. |
| Bi-Annually | Carbon Roller Disks | Check tracking limits. Replace carbon roller wheels if worn down past 50% of original cross-section thickness. |
| Annually | Core Insulation & Oil | Conduct total winding insulation resistance checks (5000 V Megger tracking) and complete an oil acidity test. |