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Operations & Maintenance (O&M) Manual

1. Equipment Handling & Storage
a. Offloading: Always utilize the welded lifting lugs located on the top panel of the tank cover. Avoid passing chains around the radiator tubes or thin outer sheet steel walls.
b. Storage Environment: If storing prior to commissioning, ensure the unit is kept in a dry, dust-free zone. Ensure all protective conduit plugs remain tightly sealed.

2. Commissioning Procedure
a. Foundation: Install the unit perfectly level on a reinforced concrete plinth designed to bear the structural operating weights detailed in Section 4
b. Earthing: Securely connect the two designated diagonal body earth terminals to separate dedicated site ground grids.
c. Control Loop Calibration: Energize the low-voltage auxiliary control circuits. Verify that the tracking voltmeter boots up accurately and the electronic sensing relays operate correctly.

3. Periodic Maintenance Matrix
	Frequency
	Target Component
	Maintenance Action Required

	Daily
	Voltmeter Panels & Gauges
	Log input/output operational terminal line matrix and inspect oil level indicators.

	Monthly
	Roller Contacts & Tracks
	Inspect carbon roller assemblies for mechanical wear tracks. Blow out any accumulation of carbon dust.

	Bi-Annually
	Carbon Roller Disks
	Check tracking limits. Replace carbon roller wheels if worn down past 50% of original cross-section thickness.

	Annually
	Core Insulation & Oil
	Conduct total winding insulation resistance checks (5000 V Megger tracking) and complete an oil acidity test.




image1.png




image2.jpeg




